## Sheet1
Calculating Pole Height
To Avoid Shading
Distance between shading object and Pathfinder* | Measured angle | Desired angle | Pole height required to achieve desired angle 2*
D | Angle 1 | Angle2 | P
10 | 50 | 22 | 7.8773
* Measurements will be caluclated in same units as input
(if "Distance" is measured in feet, "Pole Height" will also be in feet;
meters will calculate to meters, etc.).
1. Place the Solar Pathfinder (SPF) on the ground in the location of the future PV Panel.
2. Place the SPF angle estimator over the latitude-specific diagram.
3. Measure the distance from the SPF to the shading object. Type this measurement
into the spreadsheet in the blue shaded box with the "D" (distance) above it.
4. Note the current maximum altitude (angle above horizon) of the shading object
(angle 1) and type this angle measurement into the speadsheet in the red shaded
box with the "angle 1" above it.
5. With the latitude-specific diagram under the angle estimator, note the highest angle
possible (along the same azimuth) that would not cross into the sunpath arcs.
Type this angle measurement into the spreadsheet in the green shaded box
with the "angle 2" above it.
6. Pole Height ("P") in yellow box will calculate height (of bottom of panels)
required to achieve desired angle 2.
In the above example, the large tree (shading between12:30-2:00) is currently at
50 degrees altitude (between 20-25 degrees west azimuth).
December's sunpath arc for this latitude crosses the same azimuth at about 22 degrees.
If:
the distance ("D") between the future panel and the shading object is 10 feet;
"angle 1"=50
"angle 2"=22
Then, "P" (Pole Height) = 7.9